| Task | Lay ductile iron outfall pipe |
| --- | --- |
| Project/Location | Arinagour Outfall, Mull |
| Client | Scottish Water |
| Associated Documents | Drawings: Risk Assessment: Relevant Document: |

PPE to be worn at all times:

- Hard Hat

- Safety Boots

- High Viz. Vests

- Safety Glasses

- Gloves

- Full Body Coverage

- Life Jackets

Plant and personnel required for these works will include the following:

- Mechanical excavator and operator

- Foreman (Authorised Person)

- Ganger

- Labourers

- Tipping Lorry/Concrete Lorry and drivers

- Dumper

- CAT & Genie and authorised person

- Marker Spray

- Hand Tools

- Stihl Saw

- Safety Signage

- Safety Barrier

Method to be employed:

These instructions will be read prior to any commencement of work on site.  If there is any doubt as to what is required stop work immediately. Full clarification will be received before commencement of work.

- All personnel to wear suitable PPE at all times, including high visibility vests or jackets, gloves, hard hats, safety glasses & safety boots.

- A checklist of all materials, plant, pumps, barriers will be produced and to ensure the correct resources are available before work commences.

- Adequate access to the working area will be defined and suitable for construction plant & operatives.

- All plant operators to have the relevant CSCS documentation; work practices will be agreed in advance and work teams briefed accordingly. A Toolbox talk on excavation’s and working in the proximity of underground services will be carried out prior to starting on site.

- All machinery/plant to be locked/immobilized outside of normal working hours.

- We will ensure that operatives keep clear of the excavator and other site plant and that no other site operations are on-going within the reach of excavating plant.

- Access and egress routes to be agreed prior to any work commencing.

- The pipes will be delivered from the supplier by lorry and the excavator will be used to off load. Using slings attached to both the excavator and the pipe, carefully lift off the lorry and place onto the ground. Ensure that no-one is within the lifting area until the pipe has been placed. The pipe will require to be made stable to prevent it from rolling along the ground. Use timber posts or some other form of material to “chock” the sides. Store the pipes on site well away from access routes or other excavation areas.

- All lifting equipment must be checked and certified.

- All slinging must be carried out by a trained competent person.

- An authorised Person is to be present on site at all times and will be responsible for co-ordination of all vehicle movement and working practices (co-ordinating works with the Site Manager). A banks man will be in attendance for all vehicle movements within the area.

- The engineer will agree and set out location and level of proposed line and level and the excavation for the manhole will be marked with marker spray. The area marked for excavation will be CAT scanned and any live cables detected must be reported to the Site Manager before proceeding.

- The ductile Iron pipes shall be laid starting at the lowest point and working toward the highest point.

- The works on the ductile iron outfall section on the shore  will require to be laid at low tide, a small section of concrete base will be laid insitu at the positions required these will be used as a foundation for the precast units that will carry the pipe.

- The works will commence at the headwall section, this will be a precast concrete unit that will be placed by a 8t excavator. A 150mm dia tideflex valve will be fitted onto the pipe outlet.

- The precast concrete units will be carried out by an excavator and placed within the concrete.

- 150mm diameter ductile pipe will be laid on top of the precast units and strapped onto the unit with neoprene rubber and stainless steel straps and bolted onto position. The pipe laying will continue up the shore.

- Whilst laying the new pipework it will be important to make sure there is no contamination within the pipe. The operative will check for any debris inside the pipe before laying it and will remove it if there is. If the ground conditions become wet and muddy then a sump will always be excavated to make sure no dirty water runs down the new pipe, again a stopper will be used while the pipe is unattended.

- Excavations will be backfilled as soon as possible after pipe laying and any excavations left open will be protected using temporary fencing.

- The foul drains will be air-tested in accordance with ‘Sewers of Scotland 2nd Edition’. All the open ends of the drainage system will be plugged using an expandable stopper. The stoppers will be tightly fitted to prevent air loss. A drain testing kit will be used to pump air into the drainage system, to a pressure of 100mm head of water. This will be clearly shown on the test gauge. To pass the test, the reading must stay above 75mm after a period of 5 minutes without further pumping.

- The above test will be witnessed by the Clients Representative for approval.

- The new manhole will be installed during the above operations. The first precast ring will be set in concrete and following curing the remainder of the manhole will be installed as per SW detailed drawings.

- On completion the existing sewer will be connected into the new line and the redundant pipe and manhole will be removed from site. The beach will be reinstated prior to leaving site.

# Warning

There will be no deviation from this method statement unless agreed with the Principal Contractors Site Representative (& where applicable the SSE Authorised Person) and the written method statement has been revised, agreed & authorised.

(NB This section is to be signed by all personnel who are to be engaged in the works.)

I HAVE READ AND UNDERSTOOD THE REQUIREMENTS AND METHODS OF WORK TO BE CARRIED OUT AS DETAILED IN THE ABOVE METHOD STATEMENT.

WE THE UNDERSIGNED HAVE READ AND UNDERSTAND THE REQUIREMENTS AND METHODS OF WORK AS DETAILED IN THE ABOVE METHOD STATEMENT.

WE WILL REPORT TO THE PERSON IN CHARGE ANY PROPOSED DEVIATION TO THIS METHOD STATEMENT.

| Name | Signature | Date |
| --- | --- | --- |